# Legionella Management

# Risk Identification

# Checklist

# Document 52

Legionella Management Risk Identification Checklist

Based on HSG 274 (Part 2)

Schools should complete this checklist to ensure the written scheme of control is completed and managed.

It details the L8 requirements for managing the school’s water legionella management and is based on HSG 274-part 2 standard.

This table should be used as a ‘check the checker’ review to ensure that all details are recorded including what controls are in place and any actions.

Please see the example below

| Example |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No | Task | Frequency (Or as indicated by the risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| 1 | Legionella water risk assessment | 2 years | Water Management ABC Company | R. Thames (Premises Manager) | Produce and/or complete the review | Jo Blogs (School Business Manager) |

| Table 1 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No | Task | Frequency (Or as indicated by the risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| 1 | Legionella water risk assessment | 2 years |  |  | Produce and/or complete the review |  |
| 2 | Cold Water (CW) Sentinel taps water temperature | Monthly |  |  | Water temperature should be below 200C after running the water for 2 min |  |
| 3 | Hot Water (HW) Sentinel taps water temperature | Monthly |  |  | Water temperature should be above 500C after running the water for 1 min |  |
| 4 | A representative sample of the HW taps temperature | On rotation |  |  | A representative number of HW taps on rotation. Water temperature should be above 500C after running the water for 1 min |  |

(Continued)

| No | Task | Frequency (Or as indicated by the risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| --- | --- | --- | --- | --- | --- | --- |
| 5 | A representative sample of the CW taps temperature | On rotation |  |  | A representative number of CW taps was sampled on rotation. Water temperature should be below 200C after running the water for 2 min |  |
| 6 | Check thermal insulation CW system (CWS) | Annually |  |  | Check thermal insulation to ensure intact; consider weatherproofing if exposed to outside |  |
| 7 | Calorifier temperature leaving and returning (HW) | Monthly |  |  | Outgoing temperature should be above 600C and return above 500C |  |

(Continued)

| No | Task | Frequency (Or as indicated by the risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| --- | --- | --- | --- | --- | --- | --- |
| 8 | Calorifier inspection and clean | Annually |  |  | Remove the inspection cover and/or use a borescope camera and clean it by draining the vessel. Where no inspection cover: purge debris and collect the initial flush for inspection |  |
| 9 | Cold Water Tanks | Annually |  |  | Inspect and carry out remedial work. |  |
| 10 | Cold Water Tanks check the water temperature | Annually (Summer) |  |  | Check the tank water temperature remote from the ball valve and the incoming mains temperature. Water temperature should be below 200C at all times |  |
| 11 | Showers and spray taps | Quarterly |  |  | Dismantle clean and descale removable parts, heads, inserts, and hoses, if applicable |  |

| No | Task | Frequency (Or as indicated by the risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| --- | --- | --- | --- | --- | --- | --- |
| 12 | Combination water heaters | Annually |  |  | Inspect the cold-water header tanks |  |
| 13 | Combination water heaters | Monthly |  |  | Check water temperatures at an outlet to confirm the heater operates between 50-600C |  |
| 14 | Point of Use (POU) taps | Monthly or six monthly – on rotation |  |  | Check water temperatures at an outlet to confirm the heater operates between 50-600C |  |
| 15 | POU filters | According to manufacturer’s Guidelines |  |  |  |  |
| 16 | Base Exchange Softeners | Weekly |  |  | Visual check on salt levels and top up where necessary |  |

(Continued)

| No | Task | Frequency (Or as indicated by the risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| --- | --- | --- | --- | --- | --- | --- |
| 17 | Base Exchange Softeners | Annually |  |  | Service and disinfect |  |
| 18 | Multiple use filter | As recommended by the manufacturer |  |  | Backwash and regenerate as specified by the manufacturer |  |
| 19 | Infrequently used outlets | Weekly |  |  | Flush through |  |
| 20 | Thermostatic mixing valves (TMVs) | Annually or as recommended by the manufacturer |  |  | Remove and/or inspect, clean, descale, and disinfect. |  |
| 21 | Expansion Vessels | Monthly and or six-monthly |  |  | Where practical flush through |  |

| Table 2 HSG274 Part 2 Cleaning and Disinfection |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Task | Frequency (Or as indicated by risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| 22 | Cleaning and Disinfection | Annually |  |  | Chemical disinfection |  |

(Continued)

| TABLE 3 HSG274 Part 2 Microbiological Monitoring |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No. | Task | Frequency (Or as indicated by risk assessment) | Task completed by (Service provider/ School) | Managed process by (Premises Manager/ Staff) | Action point | Process checked by (Premises Manager or SBM) |
| 24 | Microbiological Monitoring BS7592 | As per the building Risk Assessment recommendations. Following a continually non-conforming temperature reading 2-7 days after disinfection of tank. |  |  | 4 x samples Following the positive sample, flush and re-test |  |

(Continued)

| Guidance Version Control |  |  |
| --- | --- | --- |
| Name Of Document | Version | Last Review date |
| Legionella Management Risk Identification Checklist | NASPM V3 | September 2024 |

Copyright © 2024 NASPM

All rights reserved.

No part of any NASPM document may be reproduced, distributed, or transmitted in any form or by any means, including photocopying, recording, or other electronic or mechanical methods, to any individual, school, or organisation outside of the school named in the school membership agreement.

Should membership terminate, no part of any NASPM document may be used, reproduced, distributed or transmitted by any individual, school, or organisation.